ARCHITECTURAL AND ENGINEERING SPECIFICATION

# Industrial Fiber-Optic Transmission System

Basis of Design: KBC Networks ASFOM-BUS

| Product family: Industrial fiber-optic transmission equipment | Document status: Tender / design specification |
| --- | --- |
| Source data: specsheet-asfom_bus-low-rev1401.pdf | Prepared: 4 August 2026 |

# PART 1 - GENERAL

## 1.1 SUMMARY

Provide, install, configure where applicable, test and commission the industrial fiber-optic transmission system described in this specification, including the required interfaces, power connections, mounting hardware and compatible accessories.

## 1.2 BASIS OF DESIGN

Basis-of-design manufacturer and product: KBC Networks ASFOM-BUS. Source description: ASFOM Bus Transmission System.

Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.

## 1.3 SUBMITTALS

Manufacturer technical data sheet identifying the exact model and selected hardware variant.

Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.

Power calculation confirming input-supply compatibility and the total connected load where applicable.

Mounting, environmental and configuration details applicable to the proposed installation.

## 1.4 QUALITY ASSURANCE

Installation shall be performed by personnel familiar with industrial fiber-optic transmission, optical power budgets, connector and wavelength selection, signal interfacing and applicable electrical and network practices. Verify all product capability from the current manufacturer data sheet and selected part number.

# PART 2 - PRODUCTS

## 2.1 REQUIRED PRODUCT

The equipment shall be KBC Networks ASFOM-BUS, or an approved equivalent meeting all requirements below. It shall be supplied as asfom bus transmission system.

## 2.2 PRODUCT DESCRIPTION

The KBC ASFOM range allows optical bus systems to be configured simply and easily. Utilizing CWDM (Coarse Wavelength Division Multiplexer) technology, up to 16 optical wavelengths can be combined in a single fiber to create an add/drop bus arrangement.

Each transmitter module must have a corresponding receiver module. In effect, the system is 16 individual point-to-point links integrated via the CWDM.

As with all ASFOM products, the system provides a path for analog video, data, analog audio, contact closure, telephone and Ethernet signals. All signals are digitized providing excellent quality and guaranteed performance throughout the system. Video is offered with 8-bit digital resolution without compression providing real-time video images across the network.

## 2.3 KEY FEATURES

Video, audio, data, telephone, contact closure, Ethernet, DVI, SDI & USB interfaces

Add-drop bus configuration

Application specific product configuration

All digital non-compressed

8 bit video encoding

Multimode and singlemode

Wall-mount, rack or chassis configurations

Unique Configurator software package

## 2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS

| Requirement | Specified performance |
| --- | --- |
| Video - Format | PAL / NTSC / SECAM |
| Telephone - Voice Encoding | 8 bits PCM encoded |
| Video - Input/Output | 1.0V pk-pk typical, 75Ω |
| Telephone - Operating | Mode Telco, PBX/telephone |
| Video - Bandwidth | 5 Hz ~ 6.5 MHz |
| Video - Digital Encoding (non compressed) | 8 bit |
| Video - Differential Gain (10-90% APL) | <2% |
| Video - Differential Phase (10-90% APL) | <2° |
| USB - Interface Standard | USB2.0 / USB1.1 |
| Video - Signal to Noise Ratio (SNR) weighted | >60dB |
| USB - Data Rate Low Speed | 1.5Mbps |
| USB - Full Speed | 12Mbps |
| USB - High Speed | 480Mbps |
| SDI - Interface Standard | SMPTE 259M, 292M, 424M |
| USB - Port Power | 500mA max |
| SDI - Input/Output | 800mV pk-pk ±15% |
| Optical - Wavelength | Single & WDM 1310nm, 1550nm |
| DVI - Interface Standard | DVI 1.0 |
| Optical - CWDM | 1310 ~ 1610nm |
| DVI - Video Display Resolution DVI | Up to 1920 x 1200 @ 60 Hz |
| Optical - Fiber | Multimode, Singlemode |
| DVI - HDTV | Up 1080p |
| Optical - Number of Fibers | 1 or 2 |
| DVI - Color Depth | 24 bit |
| DVI - Pixel Clock | 165 MHz max. |
| DVI - Video Bandwidth | 3.96 Gbps |
| DVI - DDC Standard | DDC2/EDID 1.0/2.0 |
| Power - Power Input Wall-mount | +12 Vdc |
| Power - Power Supply for Wall-mount(2) | Input: 100 ~ 240 Vac; Output +12 Vdc |
| Power - Rack Module(2) | Input: 100 ~ 240 Vac @ 2A |
| Data(1) - Data Formats | RS232, RS422, RS485 (2W & 4W) |
| Power - Chassis Card | Supplied from FR4 PSU |
| Data(1) - Number of Two-way Channels | 1 |
| Data(1) - RS-232 Data Rate | DC – 115.2 kbps |
| Environmental - Operating Temperature | -40°~ +74°C / -40°~ +165°F |
| Data(1) - RS-422/485 Data Rate | DC – 250 kbps |
| Environmental - Storage Temperature | -40°~ +74°C / -40°~ +165°F |
| Data(1) - Bit Error Rate | <1 x 10-12 |
| Environmental - Operating Humidity | 0 to 95% non-condensing |
| Data(1) - Encoding Schemes | Manchester, Bi-Phase, NRZ, NRZI |
| Mean Time - Between Failure (MTBF) | >100,000 Hours |
| Audio - Bandwidth | 10 Hz ~ 20 kHz |
| Audio - Audio Input/Output Levels | +/-9dBm, typical 0dBm |
| Dimensions - (Wall-mount L x W x H) | 221mm x 155mm x 36mm (8.7” x 6.1” x 1.42”) |
| Audio - Input Impedence | 600Ω unbalanced or balanced |
| Dimensions - Dimensions (Rack) | 1U 19” 1U |
| Audio - Output Impedence | 20kΩ unbalanced or balanced |
| Dimensions - 2U | 19” 2U |
| Audio - Digital Encoding | 24 bits (AES-3) |
| Audio - Sampling Rate | 192 kHz |
| Number of 4U - Chassis Card Slots(3) | Depends on product configuration |
| Audio - Signal to Noise Ratio | ≥80dB |
| Audio - Total Harmonic Distortion | ≤0.01% |
| Connectors - Video | BNC 75Ω |
| Connectors - SDI | BNC 75Ω |
| Connectors - DVI | DVI-I Female |
| Contact Closure - Response Time | 500μs |
| Connectors - Data | Screw Block Terminal |
| Contact Closure - Input | Dry Contact Closure, TTL |
| Connectors - Audio | Screw Block Terminal |
| Contact Closure - Output | SPST Relay, Normally Open |
| Connectors - Contact Closure | 8 Way Screw Block Terminal |
| Contact Closure - Switch Rating | 1A @ 30 Vdc max, 0.5A @ 125 Vac max |
| Connectors - Telephone | RJ11 |
| Connectors - Ethernet | RJ45 |
| Connectors - USB Transmitter | 1 x Type B |
| Connectors - Receiver | 4 x Type A |
| Ethernet - Standard | IEEE 802.3 Compliant |
| Connectors - Fiber | ST or FC (ST fitted as standard) |
| Ethernet - Data Rate | 10 / 100 Mbps auto sensing |

The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.

## 2.5 SOURCE VERIFICATION NOTE

The requirements in this document have been prepared from specsheet-asfom_bus-low-rev1401.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.

# PART 3 - EXECUTION

## 3.1 EXAMINATION

Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.

Confirm that all input-power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.

Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.

Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.

## 3.2 INSTALLATION

Confirm signal type, channel count, direction, connector, wavelength, fiber type and link distance for every optical path.

Confirm compatible transmitter, receiver, card, chassis and power-supply arrangements before installation.

Protect and route fiber in accordance with the approved drawings, maintaining bend radius and connector cleanliness.

Label all electrical interfaces, optical links, fibers, cards, chassis positions and power circuits.

## 3.3 CONFIGURATION AND COMMISSIONING

Verify operation of every electrical signal and optical path included in the system.

Measure or otherwise confirm optical link performance and verify that the installed loss is within the approved budget.

Demonstrate alarm, redundancy and recovery functions where supported.

Provide final channel schedules, optical test results and installed model/serial information.