ARCHITECTURAL AND ENGINEERING SPECIFICATION

# Industrial Fiber-Optic Transmission System

Basis of Design: KBC Networks FDVA8

| Product family: Industrial fiber-optic transmission equipment | Document status: Tender / design specification |
| --- | --- |
| Source data: specsheet-fdva8_series-low-rev1108.pdf | Prepared: 4 August 2026 |

# PART 1 - GENERAL

## 1.1 SUMMARY

Provide, install, configure where applicable, test and commission the industrial fiber-optic transmission system described in this specification, including the required interfaces, power connections, mounting hardware and compatible accessories.

## 1.2 BASIS OF DESIGN

Basis-of-design manufacturer and product: KBC Networks FDVA8. Source description: Eight Channel Video Multiplexer, Point-to-Point Transmission.

Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.

## 1.3 SUBMITTALS

Manufacturer technical data sheet identifying the exact model and selected hardware variant.

Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.

Power calculation confirming input-supply compatibility and the total connected load where applicable.

Mounting, environmental and configuration details applicable to the proposed installation.

## 1.4 QUALITY ASSURANCE

Installation shall be performed by personnel familiar with industrial fiber-optic transmission, optical power budgets, connector and wavelength selection, signal interfacing and applicable electrical and network practices. Verify all product capability from the current manufacturer data sheet and selected part number.

# PART 2 - PRODUCTS

## 2.1 REQUIRED PRODUCT

The equipment shall be KBC Networks FDVA8, or an approved equivalent meeting all requirements below. It shall be supplied as eight channel video multiplexer, point-to-point transmission.

## 2.2 PRODUCT DESCRIPTION

The KBC FDVA8 series uses the most advanced digital technologies to provide excellent, repeatable performance for today’s CCTV systems. It supports transmission of up to eight analog composite video channels over one multimode or Singlemode optical fiber. PAL, NTSC and SECAM video standards are fully supported. The plug-and-play design ensures ease of installation with no electrical or optical adjustment needed. LED indicators are provided to clearly show the operational status of the unit.

The series is available in wall mount or 3U chassis card.

## 2.3 KEY FEATURES

8 or 10 bit digitally encoded non-compressed video transmission

Multimode and singlemode solutions

LED indicators provide quick diagnosis of all important system parameters

Wall mount and 3U chassis card configurations

Wide optical dynamic range. No adjustment is required

## 2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS

| Requirement | Specified performance |
| --- | --- |
| Video - No. of Channels | 8 |
| Environmental - Operating Temperature | -40°~+74°C / -40°~+165°F |
| Video - Format | PAL / NTSC / SECAM |
| Environmental - Storage Temperature | -40°~+74°C / -40°~+165°F |
| Video - Input/Output | 1.0V pk-pk typical, 75Ω |
| Environmental - Operating Humidity | 0 to 95% non-condensing |
| Video - Bandwidth | 5 Hz ~ 6.5 MHz |
| Environmental - Mean Time Between Failure (MTBF) | >100,000 Hours |
| Video - Digital Encoding (non compressed) | 8 bit 10 bit |
| Video - Differential Gain (10-90% APL) | <2.0% <2.0% |
| Video - Differential Phase (10-90% APL) | <2.0° <0.7° |
| Video - SNR | >60dB >67dB |
| Mechanical - Dimensions (Wall-mount L x W x H) | 222mm x 155mm x 56mm (8.74” x 6.22” x 1.42”) |
| Mechanical - Number of 3U Chassis Card Slot(3) | 2 |
| Optical - Wavelength | 1310nm |
| Optical - Number of Fibers | 1 |
| Optical - Fiber | Multimode or Singlemode |
| Connectors - Video | BNC 75Ω |
| Connectors - Fiber | ST, SC or FC (ST fitted as standard) |
| Power - Power Input | Wall-mount +12Vdc |
| Power - Power Supply(1) | Input: 100 ~ 240 Vac Output: +12 Vdc UL and cUL listed PSU |
| Connectors - Power | Screw Block Terminal (Wall-mount ) |
| Power - Chassis Card | Supplied from FR3 PSU |

The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.

## 2.5 SOURCE VERIFICATION NOTE

The requirements in this document have been prepared from specsheet-fdva8_series-low-rev1108.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.

# PART 3 - EXECUTION

## 3.1 EXAMINATION

Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.

Confirm that all input-power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.

Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.

Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.

## 3.2 INSTALLATION

Confirm signal type, channel count, direction, connector, wavelength, fiber type and link distance for every optical path.

Confirm compatible transmitter, receiver, card, chassis and power-supply arrangements before installation.

Protect and route fiber in accordance with the approved drawings, maintaining bend radius and connector cleanliness.

Label all electrical interfaces, optical links, fibers, cards, chassis positions and power circuits.

## 3.3 CONFIGURATION AND COMMISSIONING

Verify operation of every electrical signal and optical path included in the system.

Measure or otherwise confirm optical link performance and verify that the installed loss is within the approved budget.

Demonstrate alarm, redundancy and recovery functions where supported.

Provide final channel schedules, optical test results and installed model/serial information.