ARCHITECTURAL AND ENGINEERING SPECIFICATION

# Industrial Fiber-Optic Transmission System

Basis of Design: KBC Networks FTC

| Product family: Industrial fiber-optic transmission equipment | Document status: Tender / design specification |
| --- | --- |
| Source data: specsheet-ftc_series-low-rev1108.pdf | Prepared: 4 August 2026 |

# PART 1 - GENERAL

## 1.1 SUMMARY

Provide, install, configure where applicable, test and commission the industrial fiber-optic transmission system described in this specification, including the required interfaces, power connections, mounting hardware and compatible accessories.

## 1.2 BASIS OF DESIGN

Basis-of-design manufacturer and product: KBC Networks FTC. Source description: CAN Bus Point-to-Point & Bus Transmission.

Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.

## 1.3 SUBMITTALS

Manufacturer technical data sheet identifying the exact model and selected hardware variant.

Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.

Power calculation confirming input-supply compatibility and the total connected load where applicable.

Mounting, environmental and configuration details applicable to the proposed installation.

## 1.4 QUALITY ASSURANCE

Installation shall be performed by personnel familiar with industrial fiber-optic transmission, optical power budgets, connector and wavelength selection, signal interfacing and applicable electrical and network practices. Verify all product capability from the current manufacturer data sheet and selected part number.

# PART 2 - PRODUCTS

## 2.1 REQUIRED PRODUCT

The equipment shall be KBC Networks FTC, or an approved equivalent meeting all requirements below. It shall be supplied as can bus point-to-point & bus transmission.

## 2.2 PRODUCT DESCRIPTION

The KBC FTC and FTCB series products provide an optical point-to-point or bus network connection for CAN bus data interfaces on one or two, multimode or singlemode optical fibers. The FTC units operate as the end or terminal points and provide an electrical connection and a two fiber

## 2.3 KEY FEATURES

Up to 1Mbps data rate

Switchable 110Ω line termination

Multimode and singlemode

Single fiber solution

Wall-mount, rack or chassis configurations

## 2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS

| Requirement | Specified performance |
| --- | --- |
| Data - Data Formats | CAN 2.0B – ISO11898 |
| Environmental - Operating Temperature | -40°~+74°C / -40°~+165°F |
| Data - Two Way Channels | 1 |
| Environmental - Storage Temperature | -40°~+74°C / -40°~+165°F |
| Data - CAN Data Rate | Up to 1 Mbps |
| Environmental - Operating Humidity | 0 to 95% non-condensing |
| Data - Bit Error Rate | <1 x 10-12 |
| Environmental - Mean Time Between Failure (MTBF) | >100,000 Hours |
| Optical - Wavelength | 1310nm or 1550nm |
| Optical - Fiber | Multimode or Singlemode |
| Dimensions (Wall-mount, DIN Rail)(5) - FTC (L x W x H) | 72mm x 59mm x 44mm (2.83” x 2.32” x 1.73”) |
| Optical - Number of Fibers | 1 or 2 (between each unit) |
| Dimensions (Wall-mount, DIN Rail)(5) - FTCB (L x W x H) | 135mm x 116mm x 36mm (5.31” x 4.57” x 1.42”) |
| Power - Power Input Wall-mount & DIN Rail | +12 Vdc @ 340mA |
| Dimensions (Wall-mount, DIN Rail)(5) - Number of 3U Chassis Card Slot(2) | 1 |
| Power - Power Supply for Wall-mount(1) | Input: 100 ~ 240 Vac Output: +12 Vdc UL and cUL listed PSU |
| Connectors - Data | 4 Way Screw Block terminal |
| Power - Rack Module(1) | Input: 100 ~ 240 Vac @ 2A |
| Connectors - Fiber | ST, SC or FC (ST fitted as standard) |
| Power - Chassis Card | Supplied from FR3 PSU |
| Connectors - Power(3) | Wall-mount & DIN Screw Block Terminal Rack IEC |

The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.

## 2.5 SOURCE VERIFICATION NOTE

The requirements in this document have been prepared from specsheet-ftc_series-low-rev1108.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.

# PART 3 - EXECUTION

## 3.1 EXAMINATION

Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.

Confirm that all input-power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.

Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.

Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.

## 3.2 INSTALLATION

Confirm signal type, channel count, direction, connector, wavelength, fiber type and link distance for every optical path.

Confirm compatible transmitter, receiver, card, chassis and power-supply arrangements before installation.

Protect and route fiber in accordance with the approved drawings, maintaining bend radius and connector cleanliness.

Label all electrical interfaces, optical links, fibers, cards, chassis positions and power circuits.

## 3.3 CONFIGURATION AND COMMISSIONING

Verify operation of every electrical signal and optical path included in the system.

Measure or otherwise confirm optical link performance and verify that the installed loss is within the approved budget.

Demonstrate alarm, redundancy and recovery functions where supported.

Provide final channel schedules, optical test results and installed model/serial information.