ARCHITECTURAL AND ENGINEERING SPECIFICATION

# Industrial Fiber-Optic Transmission System

Basis of Design: KBC Networks FTDB

| Product family: Industrial fiber-optic transmission equipment | Document status: Tender / design specification |
| --- | --- |
| Source data: specsheet-ftdb_series-low-rev1208.pdf | Prepared: 4 August 2026 |

# PART 1 - GENERAL

## 1.1 SUMMARY

Provide, install, configure where applicable, test and commission the industrial fiber-optic transmission system described in this specification, including the required interfaces, power connections, mounting hardware and compatible accessories.

## 1.2 BASIS OF DESIGN

Basis-of-design manufacturer and product: KBC Networks FTDB. Source description: Multi-Drop Bus Fiber Optic Modem.

Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.

## 1.3 SUBMITTALS

Manufacturer technical data sheet identifying the exact model and selected hardware variant.

Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.

Power calculation confirming input-supply compatibility and the total connected load where applicable.

Mounting, environmental and configuration details applicable to the proposed installation.

## 1.4 QUALITY ASSURANCE

Installation shall be performed by personnel familiar with industrial fiber-optic transmission, optical power budgets, connector and wavelength selection, signal interfacing and applicable electrical and network practices. Verify all product capability from the current manufacturer data sheet and selected part number.

# PART 2 - PRODUCTS

## 2.1 REQUIRED PRODUCT

The equipment shall be KBC Networks FTDB, or an approved equivalent meeting all requirements below. It shall be supplied as multi-drop bus fiber optic modem.

## 2.2 PRODUCT DESCRIPTION

The KBC FTDB and FTD series products provide an optical bus network for RS-232, RS-422 or RS-485 data interfaces over one

## 2.3 KEY FEATURES

Multi-protocol data interface

Switchable termination and biasing

Multimode and singlemode

Wall-mount, DIN and 3U chassis card

## 2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS

| Requirement | Specified performance |
| --- | --- |
| Data(1) - Data Formats | RS232, RS422, RS485 (2W & 4W) |
| Environmental - Operating Temperature | -40°~+74°C / -40°~+165°F |
| Environmental - Storage Temperature | -45°~+74°C / -40°~+165°F |
| Data(1) - Number of Two-way Channels | 1 |
| Environmental - Operating Humidity | 0 to 95% non-condensing |
| Data(1) - RS-232 Data Rate | 300 bps ~ 115.2 kbps |
| Environmental - Mean Time Between Failure (MTBF) | >100,000 Hours |
| Data(1) - RS-422/485 Data Rate | 300 bps ~ 230 kbps |
| Data(1) - Bit error rate | <1 x 10-12 |
| Data(1) - Encoding schemes | Manchester, Bi-Phase, NRZ, NRZI |
| Mechanical - Dimensions (L x W x H)(5) | 70mm x 61mm x 44mm (2.76” x 2.40” x 1.73”) (Wall-mount & DIN Rail) |
| Data(1) - Maximum Access Nodes | 128 |
| Mechanical - Number of 3U Chassis Card Slot(3) | FTD: 1 slot FTDB: 2 slots |
| Optical - Wavelength | 1310 / 1550nm |
| Optical - Fiber | Multimode or Singlemode |
| Optical - Number of Fibers | 1 or 2 (between each unit) |
| Connectors - Data | 4 way Screw Block Terminal |
| Connectors - Fiber | ST, SC or FC (ST fitted as standard) |
| Power - Power Input | (Wall-mount & DIN Rail) 12-24 Vac/dc |
| Connectors - Power(4) | Screw Block Terminal |
| Power - Power Supply(2) | Input: 100 ~ 240 Vac Output: +12 Vdc UL and cUL listed PSU |
| DIP Switch Settings - Data(5) | Switch selectable |
| Power - Chassis Card | Supplied from FR3 PSU |
| DIP Switch Settings - 120Ω termination | On / Off |
| DIP Switch Settings - Biasing | On / Off |

The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.

## 2.5 SOURCE VERIFICATION NOTE

The requirements in this document have been prepared from specsheet-ftdb_series-low-rev1208.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.

# PART 3 - EXECUTION

## 3.1 EXAMINATION

Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.

Confirm that all input-power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.

Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.

Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.

## 3.2 INSTALLATION

Confirm signal type, channel count, direction, connector, wavelength, fiber type and link distance for every optical path.

Confirm compatible transmitter, receiver, card, chassis and power-supply arrangements before installation.

Protect and route fiber in accordance with the approved drawings, maintaining bend radius and connector cleanliness.

Label all electrical interfaces, optical links, fibers, cards, chassis positions and power circuits.

## 3.3 CONFIGURATION AND COMMISSIONING

Verify operation of every electrical signal and optical path included in the system.

Measure or otherwise confirm optical link performance and verify that the installed loss is within the approved budget.

Demonstrate alarm, redundancy and recovery functions where supported.

Provide final channel schedules, optical test results and installed model/serial information.