ARCHITECTURAL AND ENGINEERING SPECIFICATION

# Industrial Fiber-Optic Transmission System

Basis of Design: KBC Networks FTDR

| Product family: Industrial fiber-optic transmission equipment | Document status: Tender / design specification |
| --- | --- |
| Source data: specsheet-ftdr_series-low-rev1108.pdf | Prepared: 4 August 2026 |

# PART 1 - GENERAL

## 1.1 SUMMARY

Provide, install, configure where applicable, test and commission the industrial fiber-optic transmission system described in this specification, including the required interfaces, power connections, mounting hardware and compatible accessories.

## 1.2 BASIS OF DESIGN

Basis-of-design manufacturer and product: KBC Networks FTDR. Source description: One Channel Multi Protocol Bi-Directional Data,.

Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.

## 1.3 SUBMITTALS

Manufacturer technical data sheet identifying the exact model and selected hardware variant.

Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.

Power calculation confirming input-supply compatibility and the total connected load where applicable.

Mounting, environmental and configuration details applicable to the proposed installation.

## 1.4 QUALITY ASSURANCE

Installation shall be performed by personnel familiar with industrial fiber-optic transmission, optical power budgets, connector and wavelength selection, signal interfacing and applicable electrical and network practices. Verify all product capability from the current manufacturer data sheet and selected part number.

# PART 2 - PRODUCTS

## 2.1 REQUIRED PRODUCT

The equipment shall be KBC Networks FTDR, or an approved equivalent meeting all requirements below. It shall be supplied as one channel multi protocol bi-directional data,.

## 2.2 PRODUCT DESCRIPTION

The KBC FTDR series products provide an optical self-healing ring network for RS232, RS422 and RS485 (2 wire & 4 wire) data interfaces over two multimode or singlemode optical fibers. The system offers maximum reliability as it can recover simultaneous faults or failures in two different locations and has contact closure outputs on each module to clearly indicate any fault location. The self-healing ring consists of two opposing data paths: ring A and ring B. Under normal operation only the primary path (ring A) is used for data transfer. If a fault is detected, the data is transferred to the secondary path (ring B) without interruption to the communications network. The series is available in wall-mount, DIN rail or 3U chassis card.

## 2.3 KEY FEATURES

Supports RS232, RS422 and RS485 (2W & 4W)

Multimode and singlemode solutions

Switchable 120Ω termination and biasing

Contact closure alarm outputs per station

Single or dual-fiber configurations

Wall-mount, DIN rail and 3U chassis card

## 2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS

| Requirement | Specified performance |
| --- | --- |
| Data(1) - Data Formats | RS232, RS422, RS485 (2W & 4W) |
| Environmental - Operating Temperature | -40°~+74°C / -40°~+165°F |
| Environmental - Storage Temperature | -40°~+74°C / -40°~+165°F |
| Data(1) - Number of Two-way Channels | 1 |
| Environmental - Operating Humidity | 0 to 95% non-condensing |
| Data(1) - RS232 Data Rate | DC – 115.2 kbps |
| Environmental - Mean Time Between Failure (MTBF) | >100,000 Hours |
| Data(1) - RS422/485 Data Rate(2) | DC – 250 kbps |
| Data(1) - Bit Error Rate | <1 x 10-12 |
| Data(1) - Encoding Schemes | Manchester, Bi-Phase, NRZ, NRZI |
| Mechanical - Dimensions (Wall-mount L x W x H)(7) | 70mm x 61mm x 44mm (2.76” x 2.40” x 1.73”) |
| Mechanical - Number of 3U Chassis Card Slot(4) | 2 |
| Optical - Wavelength | 1310nm |
| Optical - Fiber | Multimode or Singlemode |
| Connectors - Data | Screw Block Terminal |
| Optical - Number of Fibers | 4 (two fibers per ring) |
| Connectors - Fiber | ST, SC or FC (ST fitted as standard) |
| Connectors - Power(5) | Wall-mount Screw Block Terminal |
| Power - Power Input | Wall-mount 12-24 Vac/dc @200mA 24 Vac & 24 Vdc available |
| Power - Power Supply(3) | Input: 100 ~ 240 Vac Output: +12 Vdc UL and cUL listed PSU |
| DIP Switch Settings - Data | RS232, RS422 or RS485 (2W & 4W) |
| DIP Switch Settings - 120Ω Termination | On / Off |
| Power - Chassis Card | Supplied from FR3 PSU |
| DIP Switch Settings - Biasing | On / Off |

The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.

## 2.5 SOURCE VERIFICATION NOTE

The requirements in this document have been prepared from specsheet-ftdr_series-low-rev1108.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.

# PART 3 - EXECUTION

## 3.1 EXAMINATION

Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.

Confirm that all input-power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.

Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.

Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.

## 3.2 INSTALLATION

Confirm signal type, channel count, direction, connector, wavelength, fiber type and link distance for every optical path.

Confirm compatible transmitter, receiver, card, chassis and power-supply arrangements before installation.

Protect and route fiber in accordance with the approved drawings, maintaining bend radius and connector cleanliness.

Label all electrical interfaces, optical links, fibers, cards, chassis positions and power circuits.

## 3.3 CONFIGURATION AND COMMISSIONING

Verify operation of every electrical signal and optical path included in the system.

Measure or otherwise confirm optical link performance and verify that the installed loss is within the approved budget.

Demonstrate alarm, redundancy and recovery functions where supported.

Provide final channel schedules, optical test results and installed model/serial information.