ARCHITECTURAL AND ENGINEERING SPECIFICATION

# Industrial Ethernet Media Converter

Basis of Design: KBC Networks FTL1

| Product family: Industrial Ethernet media conversion equipment | Document status: Tender / design specification |
| --- | --- |
| Source data: Specsheet-FTL1_Series-Rev1710.pdf | Prepared: 4 August 2026 |

# PART 1 - GENERAL

## 1.1 SUMMARY

Provide, install, configure where applicable, test and commission the industrial ethernet media converter described in this specification, including the required interfaces, power connections, mounting hardware and compatible accessories.

## 1.2 BASIS OF DESIGN

Basis-of-design manufacturer and product: KBC Networks FTL1. Source description: 10/100 Ethernet Media Converter.

Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.

## 1.3 SUBMITTALS

Manufacturer technical data sheet identifying the exact model and selected hardware variant.

Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.

Power calculation confirming input-supply compatibility and the total connected load where applicable.

Mounting, environmental and configuration details applicable to the proposed installation.

## 1.4 QUALITY ASSURANCE

Installation shall be performed by personnel familiar with industrial Ethernet, copper and optical interfaces, PoE power budgeting, transceiver selection and applicable electrical and network practices. Verify all product capability from the current manufacturer data sheet and selected part number.

# PART 2 - PRODUCTS

## 2.1 REQUIRED PRODUCT

The equipment shall be KBC Networks FTL1, or an approved equivalent meeting all requirements below. It shall be supplied as 10/100 ethernet media converter.

## 2.2 PRODUCT DESCRIPTION

The KBC FTL series is a fully-ruggedized 10/100 Ethernet media converter. It supports transmission of an Ethernet channel over either one or two, multimode or singlemode optical fibers. Full duplex operation enables distances in excess of 50km on singlemode fiber. Plug-and-play design ensures ease of installation with no electrical or optical adjustment needed. LED indicators are provided to show the operational status of the unit clearly. The series is available in compact, DIN rail or 3U chassis card configurations. Up to 28 FTL media converters can be accommodated in a KBC FR3 chassis.

KBC 10/100 media converters are designed for transmission distances up to 4km for multimode fiber and 50km on singlemode fiber (for distances up to 80km, please contact us). If the media converter is to be connected to an SFP port, please contact us for advice since SFPs can vary in the level at which they saturate.

## 2.3 KEY FEATURES

Wide operational temperature range

100BASE-FX on fiber port

Ultra-compact footprint

10/100 auto-sensing

MDI / MDIX

Single and dual fiber

Dual module 3U chassis card

## 2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS

| Requirement | Specified performance |
| --- | --- |
| Standards - IEEE Standards | IEEE802.3 10Base-TX IEEE802.3u 100Base-TX & 100BASE-FX IEEE 802.3x Full duplex |
| Environmental - Operating Temperature | -40°~ +74°C / -40°~ +165°F |
| Environmental - Storage Temperature | -40°~ +74°C / -40°~ +165°F |
| Environmental - Operating Humidity | 0 to 95% non-condensing |
| Environmental - Mean Time Between Failure (MTBF) | > 100,000 Hours |
| Data - Data Format | Ethernet |
| Mechanical - Dimensions Compact (W x H x D) | 70mm x 58mm x 28mm (2.8” x 2.3” x 1.1”) |
| Data - Two Way Channels | 1 |
| Data - Data Rate | 10/100Mbps Auto-Sensing Half & Full Duplex |
| Mechanical - DIN Rail | 110mm x 87mm x 25mm (4.3” x 3.4” x 0.98”) |
| Mechanical - Number of 3U Chassis Card Slots (2) | 1 |
| Optical - Wavelength | 1310nm/1550nm |
| Optical - Fiber | Multimode or Singlemode |
| Connectors - 10/100 Electrical | RJ-45 |
| Optical - Number of Fibers | 1 or 2 |
| Connectors - Fiber | ST, SC, FC or LC (ST fitted as standard) |
| Connectors - Power (3) | Compact & DIN Rail 3-way screw block terminal |
| Power - Power Input | 12-24 Vac/dc @ 200mA |
| Power - Power Supply (1) | Input: 100 ~ 240 Vac Output: +12 Vdc |
| Power - Chassis Card | Supplied from FR3 PSU |

The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.

## 2.5 SOURCE VERIFICATION NOTE

The requirements in this document have been prepared from Specsheet-FTL1_Series-Rev1710.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.

# PART 3 - EXECUTION

## 3.1 EXAMINATION

Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.

Confirm that all input-power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.

Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.

Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.

## 3.2 INSTALLATION

Confirm copper speed, duplex mode, optical speed, connector, wavelength, fiber type and link distance for each connection.

Provide approved fixed-optic or SFP transceivers matched to the intended optical path.

Provide compatible power, protective earthing, cable management and environmental protection.

Label each converter, power circuit, copper port and optical link to match the project documentation.

## 3.3 CONFIGURATION AND COMMISSIONING

Verify link operation on every connected copper and optical interface.

Verify PoE negotiation and delivered power at each powered device where applicable.

Confirm speed, duplex, link-fault and diagnostic behaviour supported by the selected model.

Provide final link schedules, test results and installed model/serial information.