ARCHITECTURAL AND ENGINEERING SPECIFICATION

# Industrial Ethernet Media Converter

Basis of Design: KBC Networks MCGN2-P1N

| Product family: Industrial Ethernet media conversion equipment | Document status: Tender / design specification |
| --- | --- |
| Source data: Specsheet-MCGN2-P1N_Series-Rev1803.pdf | Prepared: 4 August 2026 |

# PART 1 - GENERAL

## 1.1 SUMMARY

Provide, install, configure where applicable, test and commission the industrial ethernet media converter described in this specification, including the required interfaces, power connections, mounting hardware and compatible accessories.

## 1.2 BASIS OF DESIGN

Basis-of-design manufacturer and product: KBC Networks MCGN2-P1N. Source description: Industrial two channels 10/100/1000M Ethernet Media Converter with SFP.

Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.

## 1.3 SUBMITTALS

Manufacturer technical data sheet identifying the exact model and selected hardware variant.

Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.

Power calculation confirming input-supply compatibility and the total connected load where applicable.

Mounting, environmental and configuration details applicable to the proposed installation.

## 1.4 QUALITY ASSURANCE

Installation shall be performed by personnel familiar with industrial Ethernet, copper and optical interfaces, PoE power budgeting, transceiver selection and applicable electrical and network practices. Verify all product capability from the current manufacturer data sheet and selected part number.

# PART 2 - PRODUCTS

## 2.1 REQUIRED PRODUCT

The equipment shall be KBC Networks MCGN2-P1N, or an approved equivalent meeting all requirements below. It shall be supplied as industrial two channels 10/100/1000m ethernet media converter with sfp.

## 2.2 PRODUCT DESCRIPTION

The KBC MCGN2-P1N series is an industrial two channels 10/100/1000M Ethernet media converter. It supports transmission of two channels 10/100/1000 Base-T Ethernet over SFP port, by selecting different KBC SFP modules, the media converter can be transmitted via one or two, multimode or single mode optical fibers with full duplex

The series is available in wall mount, DIN, and 2U passive rack FR2-12, or card version in 2U chassis FR2-16.

## 2.3 KEY FEATURES

10/100/1000M auto sensing

2*1000Base-TX Ports

1*1000Base-FX SFP Port

2kV Surge Protection on RJ45 electrical Port

Compatible with 1 channel 1000M media converter MCGN1 series

IP40 enclosure

Wall & DIN Mount

FR2-12 passive Rack with 12 slots or Chassis card in FR2-16 with 16 slots

## 2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS

| Requirement | Specified performance |
| --- | --- |
| Standards - IEEE Standards | IEEE802.3 10Base-TX IEEE802.3u 100Base-TX IEEE802.3ab 1000Base-TX IEEE802.3z 1000Base-FX |
| Environmental - Operating Temperature | -40° ~ +75°C |
| Environmental - Storage Temperature | -40° ~ +85°C |
| Environmental - Operating Humidity | 0 to 95% non-condensing |
| Environmental - Mean Time Between Failure (MTBF) | > 100,000 Hours |
| Electrical - Data Port | 2 |
| Environmental - Enclosure Protection | IP40 |
| Electrical - Data Rate | 10/100/1000Mbps Auto-Sensing Half & Full Duplex |
| Electrical - Surge Protection | 2kV |
| Connectors - 10/100 Electrical | RJ-45 |
| Connectors - Power | Terminal |
| Connectors - Power (3) Wall Mount/DIN Rail | Screw Block Terminal |
| Optical - 100Base-FX SFP port (1) | 1 |
| Others - Cable | CAT5 or CAT6, direct or cross cable |
| Power - Power Input | +12Vdc |
| Others - LEDs | Connection status data sending & receiving |
| Power - Power consumption | < 3W |
| Power - Power Supply (2) | Input: 100 ~ 240Vac Output: +12Vdc |
| Power - Chassis Card | Supplied from FR2 PSU |

The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.

## 2.5 SOURCE VERIFICATION NOTE

The requirements in this document have been prepared from Specsheet-MCGN2-P1N_Series-Rev1803.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.

# PART 3 - EXECUTION

## 3.1 EXAMINATION

Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.

Confirm that all input-power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.

Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.

Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.

## 3.2 INSTALLATION

Confirm copper speed, duplex mode, optical speed, connector, wavelength, fiber type and link distance for each connection.

Provide approved fixed-optic or SFP transceivers matched to the intended optical path.

Provide compatible power, protective earthing, cable management and environmental protection.

Label each converter, power circuit, copper port and optical link to match the project documentation.

## 3.3 CONFIGURATION AND COMMISSIONING

Verify link operation on every connected copper and optical interface.

Verify PoE negotiation and delivered power at each powered device where applicable.

Confirm speed, duplex, link-fault and diagnostic behaviour supported by the selected model.

Provide final link schedules, test results and installed model/serial information.