ARCHITECTURAL AND ENGINEERING SPECIFICATION

# Industrial Ethernet Media Converter

Basis of Design: KBC Networks MCLN2

| Product family: Industrial Ethernet media conversion equipment | Document status: Tender / design specification |
| --- | --- |
| Source data: Specsheet_MCLN2_Series_Rev1903.pdf | Prepared: 4 August 2026 |

# PART 1 - GENERAL

## 1.1 SUMMARY

Provide, install, configure where applicable, test and commission the industrial ethernet media converter described in this specification, including the required interfaces, power connections, mounting hardware and compatible accessories.

## 1.2 BASIS OF DESIGN

Basis-of-design manufacturer and product: KBC Networks MCLN2. Source description: Industrial two channels 10/100M Ethernet Media Converter.

Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.

## 1.3 SUBMITTALS

Manufacturer technical data sheet identifying the exact model and selected hardware variant.

Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.

Power calculation confirming input-supply compatibility and the total connected load where applicable.

Mounting, environmental and configuration details applicable to the proposed installation.

## 1.4 QUALITY ASSURANCE

Installation shall be performed by personnel familiar with industrial Ethernet, copper and optical interfaces, PoE power budgeting, transceiver selection and applicable electrical and network practices. Verify all product capability from the current manufacturer data sheet and selected part number.

# PART 2 - PRODUCTS

## 2.1 REQUIRED PRODUCT

The equipment shall be KBC Networks MCLN2, or an approved equivalent meeting all requirements below. It shall be supplied as industrial two channels 10/100m ethernet media converter.

## 2.2 PRODUCT DESCRIPTION

The KBC MCLN2 series is an industrial two channels 10/100M Ethernet media converter. It supports transmission of two channels 10/100Base-T Ethernet over either one or two, multimode or single mode optical fibers with full duplex operation. Typically the two channels media converter is installed in remote end, in head end compatible

The series is available in wall mount, DIN, and 2U passive rack FR2-12.

## 2.3 KEY FEATURES

10/100M auto sensing

2kV Surge Protection on RJ45 electrical Port

Compatible with 1 channel 10/100M media converter MCLN1 series

SM (Single Mode), and MM (Multi Mode)

1 fiber or 2 fibers

SM&MM: 1310nm/1550m for 1 fiber; 1310nm for 2 fibers

Typical SM and MM transmission distance are 20KM and 2 KM respectively. Longer distance is available

IP40 enclosure

DIN, Wall Mount

FR2-12 passive Rack with 12 slots

## 2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS

| Requirement | Specified performance |
| --- | --- |
| Standards | Power |
| IEEE Standards | IEEE802.3 10Base-TX Power Input IEEE802.3u 100Base-TX IEEE802.3u 100Base-FX |
| +12Vdc - Power Consumption | < 3W |
| +12Vdc - Power Supply (2) | Input: 100 ~ 240Vac Output: +12Vdc |
| Electrical - Data Port | 2 |
| Electrical - Data Rate | 10/100Mbps Auto-Sensing Half & Full Duplex |
| Environmental - Operating Temperature | -40° ~ +75°C |
| Electrical - Surge Protection | 2kV |
| Environmental - Storage Temperature | -40° ~ +85°C |
| Environmental - Operating Humidity | 0 to 95% non-condensing |
| Environmental - Mean Time Between Failure (MTBF) | > 100,000 Hours |
| Optical - Port | 100 Mbps |
| Optical - Wavelength | 1 fiber SM&MM:1310nm/1550nm 2 fibers SM&MM: 1310nm |
| Environmental - Enclosure Protection | IP40 |
| Optical - Fiber | 1 or 2 MM (50/62.5/125μm) SM (9/125μm) |
| Connectors - 10/100M Electrical | RJ-45 |
| Connectors - Fiber (3) | FC, SC or ST |
| Connectors - Power (4) | Screw Block Terminal |
| Optical - Typical Loss Budget | 12dB |
| Optical - Typical Distance (1) | MM: 2km SM: 20KM Longer distance is available |
| Others - Cable | CAT5 or CAT6, direct or cross cable |
| Others - LEDs | Connection status data sending & receiving |

The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.

## 2.5 SOURCE VERIFICATION NOTE

The requirements in this document have been prepared from Specsheet_MCLN2_Series_Rev1903.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.

# PART 3 - EXECUTION

## 3.1 EXAMINATION

Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.

Confirm that all input-power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.

Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.

Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.

## 3.2 INSTALLATION

Confirm copper speed, duplex mode, optical speed, connector, wavelength, fiber type and link distance for each connection.

Provide approved fixed-optic or SFP transceivers matched to the intended optical path.

Provide compatible power, protective earthing, cable management and environmental protection.

Label each converter, power circuit, copper port and optical link to match the project documentation.

## 3.3 CONFIGURATION AND COMMISSIONING

Verify link operation on every connected copper and optical interface.

Verify PoE negotiation and delivered power at each powered device where applicable.

Confirm speed, duplex, link-fault and diagnostic behaviour supported by the selected model.

Provide final link schedules, test results and installed model/serial information.