ARCHITECTURAL AND ENGINEERING SPECIFICATION

# Industrial Ethernet Media Converter

Basis of Design: KBC Networks MCLS1-P1N

| Product family: Industrial Ethernet media conversion equipment | Document status: Tender / design specification |
| --- | --- |
| Source data: Specsheet-MCLS1-P1N_Series-Rev1803.pdf | Prepared: 4 August 2026 |

# PART 1 - GENERAL

## 1.1 SUMMARY

Provide, install, configure where applicable, test and commission the industrial ethernet media converter described in this specification, including the required interfaces, power connections, mounting hardware and compatible accessories.

## 1.2 BASIS OF DESIGN

Basis-of-design manufacturer and product: KBC Networks MCLS1-P1N. Source description: Industrial one channel 10/100M POE Ethernet Media Converter with SFP.

Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.

## 1.3 SUBMITTALS

Manufacturer technical data sheet identifying the exact model and selected hardware variant.

Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.

Power calculation confirming input-supply compatibility and the total connected load where applicable.

Mounting, environmental and configuration details applicable to the proposed installation.

## 1.4 QUALITY ASSURANCE

Installation shall be performed by personnel familiar with industrial Ethernet, copper and optical interfaces, PoE power budgeting, transceiver selection and applicable electrical and network practices. Verify all product capability from the current manufacturer data sheet and selected part number.

# PART 2 - PRODUCTS

## 2.1 REQUIRED PRODUCT

The equipment shall be KBC Networks MCLS1-P1N, or an approved equivalent meeting all requirements below. It shall be supplied as industrial one channel 10/100m poe ethernet media converter with sfp.

## 2.2 PRODUCT DESCRIPTION

The KBC MCLS1-P1N series is an industrial 10/100M POE Ethernet media converter(MC) with SFP port. It supports transmission of one channel 10/100Base-T Ethernet over SFP port. By selecting different KBC SFP modules, the media converter can be transmitted via one or two, multimode or single mode optical fibers with full duplex

The series is available in wall, DIN, and 2U passive rack FR2-12. Chassis card version in FR2-16 is not available.

## 2.3 KEY FEATURES

1*10/100M auto sensing port

6kV Surge Protection on RJ45 electrical Port

POE/POE+ support

1*100Base-FX SFP port

Compatible with non POE version 10/100M media converter MCLN1 series

IP40 enclosure

Wall and DIN Mount, andFR2-12 passive Rack

## 2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS

| Requirement | Specified performance |
| --- | --- |
| Standards - IEEE Standards | IEEE802.3 10Base-TX IEEE802.3u 100Base-TX/FX IEEE802.3af,IEEE802.3at |
| Environmental - Operating Temperature | -40° ~ +75°C |
| Environmental - Storage Temperature | -40° ~ +85°C |
| Environmental - Operating Humidity | 0 to 95% non-condensing |
| Environmental - Mean Time Between Failure (MTBF) | > 100,000 Hours |
| Electrical - Data Port | 1 |
| Electrical - Data Rate | 10/100Mbps Auto-Sensing Half & Full Duplex |
| Environmental - Enclosure Protection | IP40 |
| Electrical - Surge Protection | 6kV |
| Connectors - 10/100M Electrical | RJ-45 |
| Connectors - Power (3) Wall Mount/DIN Rail | Screw Block Terminal |
| Optical - 100Base-FX SFP Port (1) | 1 |
| Others - Cable | CAT5 or CAT6, direct or cross cable |
| Power - Power Input | +48 ~ 57Vdc |
| Others - LEDs | Connection status data sending & receiving |
| Power - Power consumption | <3W (without POE) <33W (with POE) |
| Power - Power Supply (2) | Input: 100 ~ 240Vac Output: +48Vdc |

The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.

## 2.5 SOURCE VERIFICATION NOTE

The requirements in this document have been prepared from Specsheet-MCLS1-P1N_Series-Rev1803.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.

# PART 3 - EXECUTION

## 3.1 EXAMINATION

Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.

Confirm that all input-power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.

Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.

Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.

## 3.2 INSTALLATION

Confirm copper speed, duplex mode, optical speed, connector, wavelength, fiber type and link distance for each connection.

Provide approved fixed-optic or SFP transceivers matched to the intended optical path.

Provide compatible power, protective earthing, cable management and environmental protection.

Label each converter, power circuit, copper port and optical link to match the project documentation.

## 3.3 CONFIGURATION AND COMMISSIONING

Verify link operation on every connected copper and optical interface.

Verify PoE negotiation and delivered power at each powered device where applicable.

Confirm speed, duplex, link-fault and diagnostic behaviour supported by the selected model.

Provide final link schedules, test results and installed model/serial information.