ARCHITECTURAL AND ENGINEERING SPECIFICATION

# Industrial Power Solution

Basis of Design: KBC Networks RM1

| Product family: Industrial power, UPS, solar or remote-site equipment | Document status: Tender / design specification |
| --- | --- |
| Source data: specsheet-rm1_series-low-rev1409.pdf | Prepared: 4 August 2026 |

# PART 1 - GENERAL

## 1.1 SUMMARY

Provide, install, configure where applicable, test and commission the industrial power solution described in this specification, including the required interfaces, power connections, mounting hardware and compatible accessories.

## 1.2 BASIS OF DESIGN

Basis-of-design manufacturer and product: KBC Networks RM1. Source description: Remote Monitor Web-based Remote Monitor & Control System.

Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.

## 1.3 SUBMITTALS

Manufacturer technical data sheet identifying the exact model and selected hardware variant.

Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.

Power calculation confirming input-supply compatibility and the total connected load where applicable.

Mounting, environmental and configuration details applicable to the proposed installation.

## 1.4 QUALITY ASSURANCE

Installation shall be performed by personnel familiar with industrial DC power systems, load calculations, battery or solar sizing, protective devices, environmental enclosures and applicable electrical practices. Verify all product capability from the current manufacturer data sheet and selected part number.

# PART 2 - PRODUCTS

## 2.1 REQUIRED PRODUCT

The equipment shall be KBC Networks RM1, or an approved equivalent meeting all requirements below. It shall be supplied as remote monitor web-based remote monitor & control system.

## 2.2 PRODUCT DESCRIPTION

The RM1 series is a web-based remote monitoring and control system for voltage, current & temperature with built-in electrical surge protection.

The RM1 is accessed via web or SNMP to remotely monitor up to four voltages, four currents and two temperatures, and to control power to equipment via four

Two of the relays can be controlled directly via the temperature sensors for regulating the temperature of equipment such as fans or heaters. The other two allow timer settings for lights etc. or control via an integrated ping watchdog so that equipment that fails to respond to pings can be power cycled. The relays also feature a programmable one-click cycle timer which can be used to turn a device

## 2.3 KEY FEATURES

Remote measurement of current, voltage & temperature

Remotely control equipment power with 4 relays

Automatically control relays based on time / temperature / ping

Web / SNMP access

Automatic email alerts

Data logging and historical data display

DIN rail mount

Surge protection

## 2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS

| Requirement | Specified performance |
| --- | --- |
| Voltage Measurement - Voltage Terminals: V1, V2,V3,V4 | 1~80Vdc |
| Power - Requirements | 0~58Vdc Wire terminal or IEEE802.3af Class 0 PoE, 3W |
| Voltage Measurement - Measurement Accuracy | +/- 0.1V |
| Voltage Measurement - Current Terminals | I1, I2 0.1~16A |
| Management - User interface | Web browser & SNMP |
| Voltage Measurement - I3, I4 | +/-8A |
| Management - Data logging | FIFO, max 1300 data sets, programmable log interval |
| Voltage Measurement - Measurement Accuracy | +/- 0.1A |
| Temperature Measurement - Temperature Terminals: T1, T2 | -40°C ~ +125°C / -40 ~ 257°F |
| Connectors - Type | Terminal block |
| Temperature Measurement - Measurement Type | T1 Embedded |
| Connectors - Wire size | 12AWG max |
| Temperature Measurement - T2 | External sensor (included) |
| Temperature Measurement - Measurement Accuracy | +/- 0.1°C |
| Environmental - Operating Temperature | -40°C ~ +75°C / -40 ~ 167°F |
| Environmental - Humidity | 0 ~ 90% |
| Relays - Relay Terminals: R1, R2, R3, R4 | 10A dc |
| Relays - Type | Normally closed |
| Relays - Control | R1, R2 Manual or automatic based on ping or time control |
| Mechanical - Dimensions (LxWxH) | 125 x 102 x 46mm / 4.9 x 4 x 1.8” |
| Mechanical - Weight | 410g / 14.5oz |
| Relays - R3, R4 | Manual or automatic based on program temperature |

The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.

## 2.5 SOURCE VERIFICATION NOTE

The requirements in this document have been prepared from specsheet-rm1_series-low-rev1409.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.

# PART 3 - EXECUTION

## 3.1 EXAMINATION

Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.

Confirm that all input-power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.

Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.

Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.

## 3.2 INSTALLATION

Confirm the continuous and peak load, input source, output voltage, required autonomy and environmental conditions.

Verify battery, solar-array, charger, controller, inverter or DC distribution compatibility where applicable.

Provide protective earthing, overcurrent protection, isolation, cable sizing and weatherproof entry arrangements.

Install all equipment, enclosures and mounting assemblies in accordance with manufacturer instructions and approved drawings.

## 3.3 CONFIGURATION AND COMMISSIONING

Verify input, charging, output-voltage and load performance under normal operating conditions.

Verify battery autonomy, solar charging or UPS transfer operation where applicable.

Demonstrate alarm, recovery and protection functions supported by the selected system.

Provide final power calculations, settings, test results and installed model/serial information.