ARCHITECTURAL AND ENGINEERING SPECIFICATION

# Industrial Power Solution

Basis of Design: KBC Networks UPS

| Product family: Industrial power, UPS, solar or remote-site equipment | Document status: Tender / design specification |
| --- | --- |
| Source data: Specsheet-UPS_Series-Rev2403.pdf | Prepared: 4 August 2026 |

# PART 1 - GENERAL

## 1.1 SUMMARY

Provide, install, configure where applicable, test and commission the industrial power solution described in this specification, including the required interfaces, power connections, mounting hardware and compatible accessories.

## 1.2 BASIS OF DESIGN

Basis-of-design manufacturer and product: KBC Networks UPS. Source description: Outdoor UPS Backup “Nighttime Charging” Kits.

Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.

## 1.3 SUBMITTALS

Manufacturer technical data sheet identifying the exact model and selected hardware variant.

Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.

Power calculation confirming input-supply compatibility and the total connected load where applicable.

Mounting, environmental and configuration details applicable to the proposed installation.

## 1.4 QUALITY ASSURANCE

Installation shall be performed by personnel familiar with industrial DC power systems, load calculations, battery or solar sizing, protective devices, environmental enclosures and applicable electrical practices. Verify all product capability from the current manufacturer data sheet and selected part number.

# PART 2 - PRODUCTS

## 2.1 REQUIRED PRODUCT

The equipment shall be KBC Networks UPS, or an approved equivalent meeting all requirements below. It shall be supplied as outdoor ups backup “nighttime charging” kits.

## 2.2 PRODUCT DESCRIPTION

The challenge of needing to mount surveillance equipment in remote locations where a network cannot be established using traditional methods has been a niche for which KBC has provided solutions for over 25 years. Many of those same applications also lack available and constant power. Light pole power is often unavailable when the lights are off. A clean, easy and affordable alternative is an engineered UPS power kit that is specifically designed to support all the devices needing power. Once batteries are installed, all the other needed components are built-in and ready to go for the electrician to wire in high voltage to charge the battery bank at night. The equipment load powers via battery

## 2.3 KEY FEATURES

Fully assembled power kits ready to apply batteries and mount

Backplate with DIN Rail provided to mount additional equipment

AC to DC Battery Charger included and integrated; compatible with sealed lead acid or lithium iron phosphate batteries

Two different sizes of lockable enclosures available; Supports up to several days of stored power (variable based on power draw and battery bank installed)

Battery enclosure with integrated charger and other power assembly components

DC low voltage output

## 2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS

| Requirement | Specified performance |
| --- | --- |
| KBC-UAL2-12 | KBC-UAL2-24 |
| KBC-UAL5-12 | KBC-UAL5-24 |
| Enclosure - Interior dimensions | H: 21.5 in x W: 16 in x D: 13 in; 54.61 cm x 40.64 cm x |
| 33.02 cm | H: 30 in x W: 22 in x D: 13 in; 76.2 cm x 55.88 cm x 33.02 cm 33 lbs; 14.97 Kg |
| Material - Weight | 13 lbs; 5.9 Kg |
| Material - Mounting system | Integrat |
| Material - Lockable | L |
| Material - Space for batteries | H: 9.5 in x W: 13.5 in x D: 12.5 in; 31.75 cm x 34.29 c |
| ed pole/wall mounting system (included) - m x 24.13 cm | H: 19 in x W: 21 in x D: 13 in; 48.26 cm x 53.34 cm x 33.02 cm |
| Power Assembly - Battery Charger | 12, 24 or 48VDC @ 24 |
| Power Assembly - AC voltage input | 100-240V |
| Power Assembly - Power output* | 12VDC 24VDC |
| AC (step down if power input is >256V) - 12VDC | 24VDC ch also provides DIN Rail to mount additional accessories and other equipment E: SLA batteries lose up to 50% of stored energy in temperatures lower than 32° F 500 AH 480 AH (equal to ~960AH of SLA) |
| Power Assembly - Mounting surface | The power assembly is pre-mounted to a back plate whi |
| Power Assembly - Operating temp | -40° ~ +60° Celsius / -40° ~ +140° Fahrenheit NOT |
| Included/excluded - Battery type | Sealed Lead Ac |
| Included/excluded - Batt Capacity, SLA | 200 AH |
| Included/excluded - Batt Capacity, Lith | 240 AH (equal to ~480AH of SLA) |
| Included/excluded - Battery wiring | Parallel Series |
| id (SLA) or Lithium Iron Phosphate (LiFePo) - Parallel | Series AL5) use model number: KBC-B12100 per battery (add in pairs if 24V) UAL5 kits) use model number: KBC-B12250 per battery (add in pairs if 24V) kits, max 4 in UAL5) use model number LIFEPO4-100A12V (add in pairs if 24V) 4-G1-L-B; To provide 8-ports 802.3af/at and fiber uplink: ESUGS8-P2-L-B 48V 802.3af PoE: KBC-DC/DC-48M; to provide 70W: KBC-DC/DC-1256P-70W ther ESUGH2-G1-L-B for 2 ports 90W or ESUGH4-G1-L-B (4 ports 180W budget) if plug-in devices are required in the application then an es are charged. Inverters will add 15 to 20W or more to the load converting devices such as injectors or PoE output switches that Interior view of UAL series back plate Switch with 4 uninterrupted PoE to change without notice. KBC is not liable for any errors, formation is for the sole purpose of identifying the products, |
| Recommended Accessories - 100Ah Batteries | 12V Sealed Lead Acid (max two in the UAL2 kits; max 4 in U |
| Recommended Accessories - 250Ah Batteries | 12V Sealed Lead Acid (max one in UAL2-12 kit; two in both |
| Recommended Accessories - LiFePo4 Batteries | 12V 100Ah LiFePo4 lithium iron phosphate (max two in UAL2 |
| Recommended Accessories - PoE Switch | To provide 4-ports 802.3af/at (powered via 12-24VDC) ESUGS Hardened Injectors To provide passive 24vdc PoE: KBC-VE-DC/DC-24; to provide |
| Recommended Accessories - HPoE Switches | To power a device that requires 30+ watts at 52+Vdc use ei |
| Recommended Accessories - Managed switch | KBC offers a 9-36Vdc input managed PoE+ output (30W per po *NOTE: There is no AC or outlet provided – inverters are not recommended but inverter can be used to provide an AC outlet that is electrified when batteri and can cause the power to be less efficient. KBC suggests using 9-36V input power via 12/24Vdc input. Power breakers DC output to batteries AC to DC battery (potentially inte Due to ongoing technological improvements, product specifications are subject and KBC makes no warranty that the products conform to any description contain statements, or assertions concerning these Products contained herein. |

The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.

## 2.5 SOURCE VERIFICATION NOTE

The requirements in this document have been prepared from Specsheet-UPS_Series-Rev2403.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.

# PART 3 - EXECUTION

## 3.1 EXAMINATION

Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.

Confirm that all input-power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.

Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.

Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.

## 3.2 INSTALLATION

Confirm the continuous and peak load, input source, output voltage, required autonomy and environmental conditions.

Verify battery, solar-array, charger, controller, inverter or DC distribution compatibility where applicable.

Provide protective earthing, overcurrent protection, isolation, cable sizing and weatherproof entry arrangements.

Install all equipment, enclosures and mounting assemblies in accordance with manufacturer instructions and approved drawings.

## 3.3 CONFIGURATION AND COMMISSIONING

Verify input, charging, output-voltage and load performance under normal operating conditions.

Verify battery autonomy, solar charging or UPS transfer operation where applicable.

Demonstrate alarm, recovery and protection functions supported by the selected system.

Provide final power calculations, settings, test results and installed model/serial information.