ARCHITECTURAL AND ENGINEERING SPECIFICATION

# Industrial Wireless Ethernet System

Basis of Design: KBC Networks WES4HTG

| Product family: Industrial wireless Ethernet equipment | Document status: Tender / design specification |
| --- | --- |
| Source data: Specsheet-WES4HTG_Series-Rev2306.pdf | Prepared: 4 August 2026 |

# PART 1 - GENERAL

## 1.1 SUMMARY

Provide, install, configure where applicable, test and commission the industrial wireless ethernet system described in this specification, including the required interfaces, power connections, mounting hardware and compatible accessories.

## 1.2 BASIS OF DESIGN

Basis-of-design manufacturer and product: KBC Networks WES4HTG. Source description: Gigabit Point-to-Point & Point-to-Multipoint Wireless Ethernet System PoE / Non PoE.

Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.

## 1.3 SUBMITTALS

Manufacturer technical data sheet identifying the exact model and selected hardware variant.

Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.

Power calculation confirming input-supply compatibility and the total connected load where applicable.

Mounting, environmental and configuration details applicable to the proposed installation.

## 1.4 QUALITY ASSURANCE

Installation shall be performed by personnel familiar with industrial wireless Ethernet, radio planning, antenna alignment, PoE power, outdoor mounting and applicable network practices. Verify all product capability from the current manufacturer data sheet and selected part number.

# PART 2 - PRODUCTS

## 2.1 REQUIRED PRODUCT

The equipment shall be KBC Networks WES4HTG, or an approved equivalent meeting all requirements below. It shall be supplied as gigabit point-to-point & point-to-multipoint wireless ethernet system poe / non poe.

## 2.2 PRODUCT DESCRIPTION

The WES4HTG Wireless Ethernet System is a high throughput gigabit wireless transmission system that operates in the license-free, 5GHz band providing an Ethernet channel of up to 1 Gbps aggregate.

The WES4HTG firmware is configurable for product type, enabling one common unit to be configured as a client, single-point host or multipoint host.

The system is IEEE802.11ac compliant and will support up to 1 Gbps throughput due to MIMO technology (Multiple In Multiple Out) and 80 MHz spectrum width capability. WES4HTG provides high throughput connectivity for backhaul applications as well as a wide range of Ethernet devices such as megapixel/HD IP cameras, DVRs and web servers. It uses secure encryption to prevent unauthorized access to the system. WES4HTG is IEEE802.3af compliant and can also be used with a power injection module for applications where PoE is not available. The WES4HTG units are wall or pole-mountable with the included hardware.

## 2.3 KEY FEATURES

Configurable for client / singlepoint host / multipoint host

IEEE802.11ac compliant

Transmission Power Control

Up to 30dBm output power

Secure transmission: WPA2 – AES or TKIP encryption

Antenna alignment & site signal survey tools

Distance adjustment for long range transmission

Range of antenna options

Passive midspan compliant PoE support

IP66 protection class

## 2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS

| Requirement | Specified performance |
| --- | --- |
| Standards - IEEE Standards | IEEE 802.3 10BASE-T, IEEE 802.3u 100BASE-TX IEEE 802.3ab 1000BASE-T, IEEE 802.3x Full Duplex IEEE 802.11a 5GHz, IEEE 802.11h ETSI DFS & TPC IEEE 802.11n MIMO |
| Power Method - PoE version | IEEE 802.3af (PD) / Included PIM |
| Power Method - PoE cable spec | 100m on 24AWG Cat5/5e/6/6e/7 |
| Mechanical (unit) - Casing | IP66 protection |
| Mechanical (unit) - Dimensions (L x W x D) | 292mm x 146mm x 89mm /11.5” x 5.75” x 3.5” |
| Frequency - USA & Canada (FCC) U-NII3 | 5180 ~ 5240MHz, 5745 ~ 5825 MHz |
| Mechanical (unit) - Weight (17dBi unit) | 0.82kg / 1.8lb |
| Frequency - Europe | 5500 ~ 5700 MHz |
| Mechanical (unit) - Installation | Wall-mount or pole-mount |
| Frequency - Frequency Operation | Auto-select User static selectable Dynamic Frequency Selection (ETSI DFS) |
| Environmental - Operating Temperature | -40°~ +74°C / -40°~ +165°F |
| Environmental - Storage Temperature | -40°~ +90°C / -40°~ +194°F |
| Frequency - Power Output | 30dBm max (1) Transmit Power Control (ETSI TPC) |
| Environmental - Operating Humidity | 5 to 95% non-condensing |
| Environmental - Mean Time Between Failure (MTBF) | > 1,500,000 Hours |
| Frequency - Channel Bandwidth Spectrum | Selectable 20, 40 or 80MHz |
| Connectors - 10/100/1000Mbps Electrical | 1 x RJ45 |
| Antenna Options - 5dBi | Omni-directional |
| Antenna Options - 9dBi | Directional integrated patch Dual polarization Beamwidth: Azimuth:Horizontal 65°, vert 65° Elevation: Horizontal 33°, vert 33° |
| Approvals - FCC Part 15 Subpart C | Class B |
| Approvals - CE | Class B |
| EN 55024 - (IEC61000-4-2,3,4,5,6,8,11) | Electromagnetic Immunity |
| Antenna Options - 17dBi | Directional integrated patch Dual polarization Beamwidth: Azimuth:Horizontal 30°, vert 33° Elevation: Horizontal 17°, vert 17° |
| EN 55024 - EN 55022 (CISPR 22) | Electromagnetic Interference (Conduction & Radiation) |
| EN 55024 - EN 60 950: 1992+A1: 1993+A2 | Low Voltage Directive |
| System - Data throughput (2) | HT40 HT80 300Mbps 500Mbps |
| System - Latency | <10ms |
| System - Encryption | TKIP / AES encryption up to 128 bit |

The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.

## 2.5 SOURCE VERIFICATION NOTE

The requirements in this document have been prepared from Specsheet-WES4HTG_Series-Rev2306.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.

# PART 3 - EXECUTION

## 3.1 EXAMINATION

Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.

Confirm that all input-power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.

Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.

Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.

## 3.2 INSTALLATION

Confirm that the selected operating frequency, channel plan and regulatory settings are suitable for the installation region.

Confirm line of sight, mounting height, antenna orientation, cable routing, surge protection and environmental exposure.

Provide compatible PoE or DC power and verify the required power budget before energising the equipment.

Configure, align and secure wireless links in accordance with the manufacturer instructions and approved network design.

## 3.3 CONFIGURATION AND COMMISSIONING

Verify link association, signal level, throughput and stability under normal operating conditions.

Record operating mode, channel, bandwidth, addressing, security and alignment settings.

Demonstrate recovery following power interruption and verify required failover or redundancy behaviour where applicable.

Provide final configuration records, test results and installed model/serial information.