ARCHITECTURAL AND ENGINEERING SPECIFICATION

# Industrial Wireless Ethernet System

Basis of Design: KBC Networks WES5

| Product family: Industrial wireless Ethernet equipment | Document status: Tender / design specification |
| --- | --- |
| Source data: Specsheet-WES5 Series-Rev2502.pdf | Prepared: 4 August 2026 |

# PART 1 - GENERAL

## 1.1 SUMMARY

Provide, install, configure where applicable, test and commission the industrial wireless ethernet system described in this specification, including the required interfaces, power connections, mounting hardware and compatible accessories.

## 1.2 BASIS OF DESIGN

Basis-of-design manufacturer and product: KBC Networks WES5. Source description: Wi-Fi 6 802.11a/n/ac/ax Wireless Ethernet Modules.

Equivalent products may be considered only when they meet or exceed every stated interface, performance, power, environmental and mounting requirement without changing the intended system design.

## 1.3 SUBMITTALS

Manufacturer technical data sheet identifying the exact model and selected hardware variant.

Interface or connection schedule identifying the electrical, optical, wireless, power and network connections.

Power calculation confirming input-supply compatibility and the total connected load where applicable.

Mounting, environmental and configuration details applicable to the proposed installation.

## 1.4 QUALITY ASSURANCE

Installation shall be performed by personnel familiar with industrial wireless Ethernet, radio planning, antenna alignment, PoE power, outdoor mounting and applicable network practices. Verify all product capability from the current manufacturer data sheet and selected part number.

# PART 2 - PRODUCTS

## 2.1 REQUIRED PRODUCT

The equipment shall be KBC Networks WES5, or an approved equivalent meeting all requirements below. It shall be supplied as wi-fi 6 802.11a/n/ac/ax wireless ethernet modules.

## 2.2 PRODUCT DESCRIPTION

This dual-radio access point incorporates the latest Wi-Fi 6 (802.11ax) wireless Ethernet technology. As the fifth addition to KBC's wireless systems, it builds on the user-friendly design of its predecessors in the widely recognized WES3 and WES4 series. WES5 utilizes 2.4 & 5 GHz license-free frequencies.

The WES5 offers unparalleled throughput, delivering up to 2.4 Gbps (radio rate) when connected to another WES5 unit in an optimal wireless environment. Its rugged,

The WES5 units are wall or pole-mountable with the included hardware.

## 2.3 KEY FEATURES

Multiple mode configurations (Host/Client/Ad-Hoc) • Point-to-Point & Point-to-Multi Point Systems

Gigabit PoE - IEEE 802.3at/bt or Passive 48Vdc • High throughput back hauls

IEEE802.11a/n/ac/ax compliant • Megapixel IP camera networks & remote gate access

Transmission Power Control, up to 27dBm • Multi-family housing complexes; parking lots; perimeter

Integrated directional antenna (option for external detection equipment; video surveillance in elevators connection available) • Warehouses, industrial plants, water treatment facilities

Static or DFS in 5.180~5.825 GHz bands • Off grid power poles with solar-powered electronics

20; 20/40; 80; 160 MHz spectrum width options • Intercoms with integrated video

Up to 2402 Mbps of Throughput • Building to building network extension

Secure transmission: WPA3 AES encryption • Exterior access points

Distance adjustment for long range transmission

IP66 protection class Included with Each Unit

Embedded web browser graphical user interface (GUI) for • Quick start instructions. at-a-glance diagnostics and ease-of-use configuration • Rugged pole/wall mount assembly kit

Static & dynamic IPv4 LAN addressing, DHCP router mode • Embedded web browser-based Graphical User Interface Contact KBC Networks for Pre-configured Point-to-Point kits and convenient bundled kits with remote power solutions providing all the needed equipment from one supplier

## 2.4 SOURCE-VERIFIED TECHNICAL REQUIREMENTS

| Requirement | Specified performance |
| --- | --- |
| Standards - IEEE Standards | IEEE 802.3 10BASE-T, IEEE 802.3u 100BASE-TX IEEE 802.3ab 1000BASE-T, IEEE 802.3x Full Duplex IEEE 802.11a 5GHz, IEEE 802.11h ETSI DFS & TPC IEEE 802.11n MIMO IEEE 802.11ac MIMO IEEE 802.11ax MU-MIMO OFDMA |
| Power Method - 48~54VDC PoE | IEEE 802.3af/at/bt (PD) PoE via PSE device |
| Power Method - 48VDC passive PoE | Gigabit PoE injector (4) |
| Consumption - 802.3af PoE | Max 14.4W, typical 7W (5) |
| Consumption - 48VDC passive PoE | Max 14.4W, typical 7W (5) |
| Casing - Dimensions (L x W x D) | 268.45mm x 130.00mm x 82.20mm /10.57” x 5.12” x 3.24” |
| Radio 1 (Wi-Fi-0) - Power Output | 27 dBm max(1) Transmit Power Control (ETSI TPC) |
| Frequency Operation - User Static Selectable | 2400~2480 MHz |
| Casing - Weight (17dBi unit) | 1.545kg / 3.41lbs |
| Casing - Installation | Wall-mount or pole-mount |
| Environmental - Protection | IP66 |
| Radio 2 (Wi-Fi-1) - Power Output | 27 dBm max(1) Transmit Power Control (ETSI TPC) |
| Environmental - Operating Temperature | -40°~ +74°C / -40°~ +165°F |
| Environmental - Storage Temperature | -40°~ +90°C / -40°~ +194°F |
| Radio 2 (Wi-Fi-1) - Channel Bandwidth Spectrum | 20/40/80/160(2) MHz selectable |
| Environmental - Operating Humidity | 5 to 95% non-condensing |
| Environmental - Mean Time Between Failure (MTBF) | > 100,000 Hours |
| Frequency Operation - User Static Selectable | 5180~5240 MHz |
| Frequency Operation - Frequencies (FCC) U-NII3 | 5745~5825 MHz |
| Frequency Operation - Dynamic Frequency | 5500~5700 MHz |
| Connectors - 10/100/1000Mbps Electrical | 1 x RJ45 |
| Connectors - N female | 2; WES5-AX-AF model only |
| Antenna Options - 5 dBi omni-directional | Dual polarization |
| Approvals - FCC Part 15 Subpart C | Class B |
| Antenna Options - External N-connector | Beamwidth |
| Approvals - CE | Class B |
| Antenna Options - (WES5-AX-AF only) | Azimuth: Horizontal 360°, vert 65° Elevation: Horizontal33°, vert 33° |
| EN 55024 - (IEC61000-4-2,3,4,5,6,8,11) | Electromagnetic Immunity |
| EN 55024 - EN 55022 (CISPR 22) | Electromagnetic Interference (Conduction & Radiation) |
| Antenna Options - 9 dBi | Dual polarization |
| Antenna Options - Integrated directional panel | Beamwidth |
| EN 55024 - EN 60 950: 1992+A1: 1993+A2 | Low Voltage Directive |
| Antenna Options - (WES5-AX-Bx model) | Azimuth: Horizontal 65°, vert 65° Elevation: Horizontal 33°, vert 33° |
| Antenna Options - 17 dBi | Dual polarization |
| Antenna Options - Integrated | Beamwidth |
| Antenna Options - directional | Azimuth: Horizontal 30°, vert 33° |
| Antenna Options - panel | Elevation: Horizontal 17°, vert 17° |
| TX/RX - Rate (3) | 2402Mbps |
| TX/RX - Latency | <10ms |
| TX/RX - Encryption | AES3 128-bit |

The installer shall verify the selected part number, accessories and all project-specific operating limits against the current manufacturer data sheet before procurement and installation.

## 2.5 SOURCE VERIFICATION NOTE

The requirements in this document have been prepared from Specsheet-WES5 Series-Rev2502.pdf. Any configurable channel count, optical module, antenna, power supply, plug, mounting option, battery, solar array, accessory or regional variant shall be selected and confirmed separately where the source sheet presents multiple possibilities.

# PART 3 - EXECUTION

## 3.1 EXAMINATION

Confirm that the proposed equipment and selected variant match the approved design, required interfaces and intended operating environment.

Confirm that all input-power, cable, fiber, antenna, network and mounting conditions are within the manufacturer limits.

Confirm that all required accessories, transceivers, power supplies, batteries, antennas, mounting components and interconnection items are available and compatible.

Do not begin installation until conflicts between the design, site conditions and manufacturer requirements have been resolved.

## 3.2 INSTALLATION

Confirm that the selected operating frequency, channel plan and regulatory settings are suitable for the installation region.

Confirm line of sight, mounting height, antenna orientation, cable routing, surge protection and environmental exposure.

Provide compatible PoE or DC power and verify the required power budget before energising the equipment.

Configure, align and secure wireless links in accordance with the manufacturer instructions and approved network design.

## 3.3 CONFIGURATION AND COMMISSIONING

Verify link association, signal level, throughput and stability under normal operating conditions.

Record operating mode, channel, bandwidth, addressing, security and alignment settings.

Demonstrate recovery following power interruption and verify required failover or redundancy behaviour where applicable.

Provide final configuration records, test results and installed model/serial information.